| Document Title: | How to set ESMPRO Agent to produce alert to Manager (in-Band method) |
| --- | --- |
| Document ID: | TID0310071000 |
| Creation Date: | 07 October 2003 |
| Modified Date: | 15 may 2007 |
| Document Revision: | 0 |
| Product Class: | Servers |
| Product and Version: | Express5800 Servers and NovaScale Servers |

ESMPRO overview

ESMPRO is a NEC monitoring software based on two modules:

- ESMPro Agent running on server side

- ESMPro Manager running on management station.

Both modules are exchanging information through SNMP protocol. The purpose of this document is to explain how to have alerts from server going to a management station linked through a permanent TCP/IP connection (In-band).

In this document, the initial environment considered is:

- ESMPRO Agent installed on Server

- SNMP protocol installed and set properly on both Server and Desktop.

- ESMPRO Manager installed on management station and Autodiscover has been done successfully.

For details about these settings, refer to ESMPRO User Guide on Express Builder CD.

Configuring ESMPRO Agent

Once ESMPRO agent installed on Server side, following items have to be configured:

- Destination settings

- Local Event to be monitored

Destination settings

- Open Agent properties (Control Panel / Icon ESMPRO Agent)

- Click “Report Settings”, a windows opens then click “Settings”/”Destination settings”. Note that a default group of IDs (“Manager”) already exists. This group will be used here but needs settings changes.

- Select “TCP/IP In-Band” and click “Adress”

- Enter either IP address or NetBIOS name of Manager and click OK and Close.

Now, the agent will report to Management Station.

Note: IP Port is by default 31134, you may change for compatibility with firewalls.

Note: NEC advise to do a test to check connectivity

See also

See TID0705041331, to add new event in alert

| Document owner: | COE Servers |
| --- | --- |
| Applies to: | Express5800 Servers, NovaScale Servers |

# Text boxes

Technical Information Document

COE

Servers